Copyright 2021 by The American Institute of Architects (AIA)

Exclusively published and distributed by Deltek, Inc. for the AIA

SECTION 312000 - EARTH MOVING

TIPS:

To view non-printing Editor's Notes that provide guidance for editing, click on MasterWorks/Single-File Formatting/Toggle/Editor's Notes.

To read detailed research, technical information about products and materials, and coordination checklists, click on MasterWorks/Supporting Information.

Content Requests:

<Double click here to submit questions, comments, or suggested edits to this Section.>

Revise this Section by deleting and inserting text to meet Project-specific requirements.

- GENERAL

      - SUMMARY

        - Section Includes:

          - Excavating and filling for rough grading the Site.

          - Preparing subgrades for [slabs-on-grade] [walks] [pavements] [turf and grasses] [and] [plants].

          - Excavating and backfilling for buildings and structures.

          - Drainage course for concrete slabs-on-grade.

          - Subbase course for concrete [walks] [pavements].

          - Subbase course[ and base course] for asphalt paving.

          - Subsurface drainage backfill for walls and trenches.

          - Excavating and backfilling trenches for utilities and pits for buried utility structures.

Retain subparagraph below if elevator work includes in-ground cylinder but cylinder excavation (normally part of elevator work) is not part of elevator work.

          - Excavating well hole to accommodate elevator-cylinder assembly.

        - Related Requirements:

Retain subparagraphs below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

          - [Section 013200 "Construction Progress Documentation"] [Section 013233 "Photographic Documentation"] for recording preexcavation and earth-moving progress.

          - Section 311000 "Site Clearing" for site stripping, grubbing, stripping[ and stockpiling] topsoil, and removal of above- and below-grade improvements and utilities.

          - Section 315000 "Excavation Support and Protection" for shoring, bracing, and sheet piling of excavations.

          - Section 316329 "Drilled Concrete Piers and Shafts" for excavation of shafts and disposal of surplus excavated material.

          - Section 329200 "Turf and Grasses" for finish grading in turf and grass areas, including preparing and placing planting soil for turf areas.

          - Section 329300 "Plants" for finish grading in planting areas and tree and shrub pit excavation and planting.

      - UNIT PRICES

Retain this article if unit prices are required for rock excavation or if authorized additional excavation is anticipated.

        - Work of this Section is affected by unit prices for earth moving specified in Section 012200 "Unit Prices."

        - Quantity allowances for earth moving are included in Section 012100 "Allowances."

Retain "Rock Measurement" Paragraph below for classified excavation. Measurements are examples only; revise dimensions to suit Project conditions and office standards. Consider separate unit prices for open rock excavation and trench rock excavation.

        - Rock Measurement: Volume of rock actually removed, measured in original position, but not to exceed the following. Unit prices for rock excavation include replacement with approved materials.

          - [24 inches (600 mm)] <Insert dimension> outside of concrete forms other than at footings.

          - [12 inches (300 mm)] <Insert dimension> outside of concrete forms at footings.

          - [6 inches (150 mm)] <Insert dimension> outside of minimum required dimensions of concrete cast against grade.

          - Outside dimensions of concrete walls indicated to be cast against rock without forms or exterior waterproofing treatments.

          - [6 inches (150 mm)] <Insert dimension> beneath bottom of concrete slabs-on-grade.

          - [6 inches (150 mm)] <Insert dimension> beneath pipe in trenches, and the greater of [24 inches (600 mm)] <Insert dimension> wider than pipe or [42 inches (1065 mm)] <Insert dimension> wide.

      - DEFINITIONS

Retain definitions remaining after this Section has been edited. Revise to suit office or local earth-moving practices.

        - Backfill: Soil material or controlled low-strength material used to fill an excavation.

          - Initial Backfill: Backfill placed beside and over pipe in a trench, including haunches to support sides of pipe.

          - Final Backfill: Backfill placed over initial backfill to fill a trench.

        - Base Course: Aggregate layer placed between the subbase course and hot-mix asphalt paving.

        - Bedding Course: Aggregate layer placed over the excavated subgrade in a trench before laying pipe.

        - Borrow Soil: Satisfactory soil imported from off-site for use as fill or backfill.

Consider revising "Drainage Course" Paragraph below and throughout this Section to suit Project or office standard. See Evaluations.

        - Drainage Course: Aggregate layer supporting the slab-on-grade that also minimizes upward capillary flow of pore water.

        - Excavation: Removal of material encountered above subgrade elevations and to lines and dimensions indicated.

          - Authorized Additional Excavation: Excavation below subgrade elevations or beyond indicated lines and dimensions as directed by Architect. Authorized additional excavation and replacement material will be paid for according to Contract provisions for [unit prices] [changes in the Work].

          - Bulk Excavation: Excavation more than [10 feet (3 m)] <Insert dimension> in width and more than [30 feet (9 m)] <Insert dimension> in length.

          - Unauthorized Excavation: Excavation below subgrade elevations or beyond indicated lines and dimensions without direction by Architect. Unauthorized excavation, as well as remedial work directed by Architect, will be without additional compensation.

        - Fill: Soil materials used to raise existing grades.

        - Rock:

Retain one of first two subparagraphs below for classified excavation. See Evaluations.

Retain first subparagraph if performance of Contractor's equipment is used to define the term "rock."

          - Rock material in beds, ledges, unstratified masses, conglomerate deposits, and boulders of rock material that exceed [1 cu. yd. (0.76 cu. m)] <Insert volume> for bulk excavation or [3/4 cu. yd. (0.57 cu. m)] <Insert volume> for footing, trench, and pit excavation that cannot be removed by rock-excavating equipment equivalent to the following in size and performance ratings, without systematic drilling, ram hammering, ripping, or blasting, when permitted:

Retain "Equipment for Footing, Trench, and Pit Excavation" Subparagraph below for confined excavation. Revise size and performance ratings of equipment to suit Project; ratings are based on Caterpillar's Model No. 320CL or Model No. 320DL.

            - Equipment for Footing, Trench, and Pit Excavation: Late-model, track-mounted hydraulic excavator; equipped with a 42-inch- (1065-mm-) maximum-width, short-tip-radius rock bucket; rated at not less than 138-hp (103-kW) flywheel power with bucket-curling force of not less than 28,700 lbf (128 kN) and stick-crowd force of not less than 18,400 lbf (82 kN) with extra-long reach boom.

Retain "Equipment for Bulk Excavation" Subparagraph below for mass or bulk excavation. Revise size and performance ratings of equipment to suit Project; ratings are based on Caterpillar's Model No. 973C.

            - Equipment for Bulk Excavation: Late-model, track-mounted loader; rated at not less than 230-hp (172-kW) flywheel power and developing a minimum of 47,992-lbf (213.3-kN) breakout force with a general-purpose bare bucket.

Retain subparagraph below if standard penetration values are used to define the term "rock." Revise number of blows or penetration resistance to suit office practice. No correlation is intended between equipment- and geotechnical-based definitions of "rock"; both are arbitrary values chosen to standardize criteria for defining "rock."

          - Rock material in beds, ledges, unstratified masses, conglomerate deposits, and boulders of rock material [3/4 cu. yd. (0.57 cu. m)] <Insert volume> or more in volume that exceed a standard penetration resistance of [100 blows/2 inches (97 blows/50 mm)] <Insert value> when tested by a geotechnical testing agency, according to ASTM D1586.

        - Structures: Buildings, footings, foundations, retaining walls, slabs, tanks, curbs, mechanical and electrical appurtenances, or other fabricated stationary features constructed above or below the ground surface.

        - Subbase Course: Aggregate layer placed between the subgrade and base course for hot-mix asphalt pavement, or aggregate layer placed between the subgrade and a cement concrete pavement or a cement concrete or hot-mix asphalt walk.

        - Subgrade: Uppermost surface of an excavation or the top surface of a fill or backfill immediately below subbase, drainage fill, drainage course, or topsoil materials.

        - Utilities: On-site underground pipes, conduits, ducts, and cables as well as underground services within buildings.

      - PREINSTALLATION MEETINGS

Retain "Preinstallation Conference" Paragraph below if Work of this Section is extensive or complex enough to justify a preexcavation conference.

        - Preinstallation Conference: Conduct preexcavation conference at [Project site] <Insert location>.

Retain subparagraph below if additional requirements are necessary; include information about conference.

          - Review methods and procedures related to earthmoving, including, but not limited to, the following:

            - Personnel and equipment needed to make progress and avoid delays.

            - Coordination of Work with utility locator service.

            - Coordination of Work and equipment movement with the locations of tree- and plant-protection zones.

            - Extent of trenching by hand or with air spade.

            - Field quality control.

            - <Insert agenda items>.

If needed, insert list of conference participants not mentioned in Section 013100 "Project Management and Coordination."

      - ACTION SUBMITTALS

        - Product Data: For each type of the following manufactured products required:

          - Geotextiles.

          - Controlled low-strength material, including design mixture.

          - Geofoam.

          - Warning tapes.

        - Samples for Verification: For the following products, in sizes indicated below:

          - Geotextile: 12 by 12 inches (300 by 300 mm).

          - Warning Tape: 12 inches (300 mm) long; of each color.

      - INFORMATIONAL SUBMITTALS

Coordinate "Qualification Data" Paragraph below with qualification requirements in Section 014000 "Quality Requirements" and as supplemented in "Quality Assurance" Article.

        - Qualification Data: For qualified testing agency.

Retain "Material Test Reports" Paragraph below for material test reports that are Contractor's responsibility.

        - Material Test Reports: For each [on-site] [and] [borrow] soil material proposed for fill and backfill as follows:

Retain both subparagraphs below for borrow soil material. Delete if using only on-site soil material and geotechnical report is sufficient.

          - Classification according to ASTM D2487.

          - Laboratory compaction curve according to [ASTM D698] [ASTM D1557].

Retain one or both of first two paragraphs below if explosives are permitted. Retain second paragraph only if seismic survey is required with blasting.

        - Blasting plan[ approved by authorities having jurisdiction].

        - Seismic survey report from seismic survey agency.

        - Preexcavation Photographs or Videotape: Show existing conditions of adjoining construction and site improvements, including finish surfaces that might be misconstrued as damage caused by earth-moving operations. Submit before earth moving begins.

      - QUALITY ASSURANCE

Retain "Blasting" Paragraph below if explosives are permitted.

        - Blasting: Comply with applicable requirements in NFPA 495, "Explosive Materials Code," and prepare a blasting plan reporting the following:

          - Types of explosive and sizes of charge to be used in each area of rock removal, types of blasting mats, sequence of blasting operations, and procedures that will prevent damage to site improvements and structures on Project site and adjacent properties.

          - Seismographic monitoring during blasting operations.

Retain "Seismic Survey Agency" Paragraph below if rock is anticipated, explosives are permitted, and independent oversight is required. Revise reporting requirements to suit Project.

        - Seismic Survey Agency: An independent testing agency, acceptable to authorities having jurisdiction, experienced in seismic surveys and blasting procedures to perform the following services:

          - Report types of explosive and sizes of charge to be used in each area of rock removal, types of blasting mats, sequence of blasting operations, and procedures that will prevent damage to site improvements and structures on Project site and adjacent properties.

          - Seismographic monitoring during blasting operations.

Retain "Geotechnical Testing Agency Qualifications" Paragraph below if Contractor selects agency for rock-definition testing. Qualification requirements are in addition to those specified in Section 014000 "Quality Requirements."

        - Geotechnical Testing Agency Qualifications: Qualified according to ASTM E329 and ASTM D3740 for testing indicated.

      - FIELD CONDITIONS

        - Traffic: Minimize interference with adjoining roads, streets, walks, and other adjacent occupied or used facilities during earth-moving operations.

          - Do not close or obstruct streets, walks, or other adjacent occupied or used facilities without permission from Owner and authorities having jurisdiction.

          - Provide alternate routes around closed or obstructed traffic ways if required by Owner or authorities having jurisdiction.

Retain "Improvements on Adjoining Property" Paragraph below to suit Project; coordinate with Owner.

        - Improvements on Adjoining Property: Authority for performing earth moving indicated on property adjoining Owner's property will be obtained by Owner before award of Contract.

          - Do not proceed with work on adjoining property until directed by Architect.

Retain "Utility Locator Service" Paragraph below if required and not specified in Section 311000 "Site Clearing"; revise to suit Project. First option is a generic term that is known in various states by different names listed in the other options. See Evaluations.

        - Utility Locator Service: Notify [utility locator service] ["Miss Utility"] ["Call Before You Dig"] ["Dig Safe System"] ["One Call"] <Insert name> for area where Project is located before beginning earth-moving operations.

        - Do not commence earth-moving operations until temporary site fencing and erosion- and sedimentation-control measures specified in [Section 015000 "Temporary Facilities and Controls"] [and] [Section 311000 "Site Clearing"] are in place.

Retain first paragraph below if protection zones and protection-zone fencing are required.

        - Do not commence earth-moving operations until plant-protection measures specified in Section 015639 "Temporary Tree and Plant Protection" are in place.

Retain three paragraphs below if tree- or plant-protection zones are required.

        - The following practices are prohibited within protection zones:

Revise subparagraphs below to suit Project.

          - Storage of construction materials, debris, or excavated material.

          - Parking vehicles or equipment.

          - Foot traffic.

          - Erection of sheds or structures.

          - Impoundment of water.

          - Excavation or other digging unless otherwise indicated.

          - Attachment of signs to or wrapping materials around trees or plants unless otherwise indicated.

        - Do not direct vehicle or equipment exhaust towards protection zones.

        - Prohibit heat sources, flames, ignition sources, and smoking within or near protection zones.

- PRODUCTS

      - SOIL MATERIALS

        - General: Provide borrow soil materials when sufficient satisfactory soil materials are not available from excavations.

Revise "Satisfactory Soils" and "Unsatisfactory Soils" paragraphs below and identify soil materials according to geotechnical engineer's written recommendations. Revise soil groups and size of stone to suit Project. Most soils are classified according to ASTM D2487. Heavy civil or highway projects may use AASHTO M 145.

        - Satisfactory Soils: Soil Classification [Groups GW, GP, GM, SW, SP, and SM according to ASTM D2487] [Groups A-1, A-2-4, A-2-5, and A-3 according to AASHTO M 145], or a combination of these groups; free of rock or gravel larger than [3 inches (75 mm)] <Insert dimension> in any dimension, debris, waste, frozen materials, vegetation, and other deleterious matter.

Retain "Liquid Limit" and "Plasticity Index" subparagraphs below if required to further qualify satisfactory soil groups.

          - Liquid Limit: <Insert value>.

          - Plasticity Index: <Insert value>.

        - Unsatisfactory Soils: Soil Classification [Groups GC, SC, CL, ML, OL, CH, MH, OH, and PT according to ASTM D2487] [Groups A-2-6, A-2-7, A-4, A-5, A-6, and A-7 according to AASHTO M 145], or a combination of these groups.

          - Unsatisfactory soils also include satisfactory soils not maintained within 2 percent of optimum moisture content at time of compaction.

Terms, descriptions, and gradations of granular soil materials in remaining paragraphs are examples only. Revise to comply with local practices and to suit Project. For example, granular materials may be referenced by state or local highway designations rather than by ASTM classifications.

        - Subbase Material: Naturally or artificially graded mixture of natural or crushed gravel, crushed stone, and natural or crushed sand; ASTM D2940/D2940M; with at least 90 percent passing a 1-1/2-inch (37.5-mm) sieve and not more than 12 percent passing a No. 200 (0.075-mm) sieve.

        - Base Course: Naturally or artificially graded mixture of natural or crushed gravel, crushed stone, and natural or crushed sand; ASTM D2940/D2940M; with at least 95 percent passing a 1-1/2-inch (37.5-mm) sieve and not more than 8 percent passing a No. 200 (0.075-mm) sieve.

        - Engineered Fill: Naturally or artificially graded mixture of natural or crushed gravel, crushed stone, and natural or crushed sand; ASTM D2940/D2940M; with at least 90 percent passing a 1-1/2-inch (37.5-mm) sieve and not more than 12 percent passing a No. 200 (0.075-mm) sieve.

        - Bedding Course: Naturally or artificially graded mixture of natural or crushed gravel, crushed stone, and natural or crushed sand; ASTM D2940/D2940M; except with 100 percent passing a 1-inch (25-mm) sieve and not more than 8 percent passing a No. 200 (0.075-mm) sieve.

        - Drainage Course: Narrowly graded mixture of [washed ]crushed stone, or crushed or uncrushed gravel; ASTM D448; coarse-aggregate grading Size 57; with 100 percent passing a 1-1/2-inch (37.5-mm) sieve and zero to 5 percent passing a No. 8 (2.36-mm) sieve.

        - Filter Material: Narrowly graded mixture of natural or crushed gravel, or crushed stone and natural sand; ASTM D448; coarse-aggregate grading Size 67; with 100 percent passing a 1-inch (25-mm) sieve and zero to 5 percent passing a No. 4 (4.75-mm) sieve.

        - Sand: ASTM C33/C33M; fine aggregate.

        - Impervious Fill: Clayey gravel and sand mixture capable of compacting to a dense state.

      - GEOTEXTILES

Retain "Subsurface Drainage Geotextile" Paragraph below if nonwoven geotextile is used in subsurface drainage applications. Delete paragraph if only factory-fabricated drainage panels are used and specified in waterproofing Sections.

Performance requirements in AASHTO M 288 have been widely adopted by geotextile manufacturers and are repeated below. The geotechnical report may also include geotextile recommendations. See Evaluations for list of geotextile manufacturers.

        - Subsurface Drainage Geotextile: Nonwoven needle-punched geotextile, manufactured for subsurface drainage applications, made from polyolefins or polyesters; with elongation greater than 50 percent; complying with AASHTO M 288 and the following, measured per test methods referenced:

          - Survivability:

Retain one of first two subparagraphs below. Survivability rates a geotextile's ability to withstand installation stresses and is measured by grab, seam, tear, and puncture strength.

Retain first subparagraph if AASHTO M 288 survivability classification is required. Survivability is divided into three classes by AASHTO M 288. Class 2 is the default class recommended by AASHTO M 288 for subsurface drainage applications. Revise to Class 1 if higher strength is required or Class 3 if lower strength is permitted.

            - Class 2; AASHTO M 288.

Strength values in first subparagraph below correspond to AASHTO M 288 Survivability Class 2 for subsurface drainage applications. Revise if other strength values are required.

            - As follows:

              - Grab Tensile Strength: 157 lbf (700 N); ASTM D4632.

              - Sewn Seam Strength: 142 lbf (630 N); ASTM D4632.

              - Tear Strength: 56 lbf (250 N); ASTM D4533.

              - Puncture Strength: 56 lbf (250 N); ASTM D4833.

AASHTO M 288 bases selection of apparent opening size for subsurface drainage geotextiles on percentages of backfill soils passing a No. 200 (0.075-mm) sieve. First option in "Apparent Opening Size" Subparagraph below corresponds to less than 15 percent; second, to 15 to 50 percent; and third, to greater than 50 percent for Class 2 geotextiles.

            - Apparent Opening Size: [No. 40 (0.425-mm)] [No. 60 (0.250-mm)] [No. 70 (0.212-mm)] sieve, maximum; ASTM D4751.

AASHTO M 288 bases selection of permittivity for subsurface drainage geotextiles on percentages of backfill soils passing a No. 200 (0.075-mm) sieve. First option in "Permittivity" Subparagraph below corresponds to less than 15 percent; second, to 15 to 50 percent; and third, to greater than 50 percent for Class 2 geotextiles.

            - Permittivity: [0.5] [0.2] [0.1] per second, minimum; ASTM D4491.

Requirement in "UV Stability" Subparagraph below corresponds to default value in AASHTO M 288 for Class 2 subsurface drainage geotextiles.

            - UV Stability: 50 percent after 500 hours' exposure; ASTM D4355.

Retain "Separation Geotextile" Paragraph below if a separation geotextile is required. A typical use is to separate subgrade from granular soil materials, such as subbase course, base course, or engineered fill. The geotechnical report may also include geotextile recommendations. See Evaluations for list of geotextile manufacturers.

        - Separation Geotextile: Woven geotextile fabric, manufactured for separation applications, made from polyolefins or polyesters; with elongation less than 50 percent; complying with AASHTO M 288 and the following, measured per test methods referenced:

          - Survivability:

Retain one of first two subparagraphs below. Survivability rates a geotextile's ability to withstand installation stresses and is measured by grab, seam, tear, and puncture strength.

Retain first subparagraph if AASHTO M 288 survivability classification is required. Survivability is divided into three classes by AASHTO M 288. Class 2 is the default class recommended by AASHTO M 288 for separation geotextile applications.

            - Class 2; AASHTO M 288.

Strength values in first subparagraph below correspond to AASHTO M 288 Survivability Class 2 for separation geotextile applications. Revise if other strength values are required.

            - As follows:

              - Grab Tensile Strength: 247 lbf (1100 N); ASTM D4632.

              - Sewn Seam Strength: 222 lbf (990 N); ASTM D4632.

              - Tear Strength: 90 lbf (400 N); ASTM D4533.

              - Puncture Strength: 90 lbf (400 N); ASTM D4833.

Requirements in "Apparent Opening Size," "Permittivity," and "UV Stability" subparagraphs below correspond to default values in AASHTO M 288 for Class 2 separation geotextiles.

            - Apparent Opening Size: No. 60 (0.250-mm) sieve, maximum; ASTM D4751.

            - Permittivity: 0.02 per second, minimum; ASTM D4491.

            - UV Stability: 50 percent after 500 hours' exposure; ASTM D4355.

      - CONTROLLED LOW-STRENGTH MATERIAL

        - Controlled Low-Strength Material: Self-compacting[, cellular, low-density], flowable concrete material produced from the following:

          - Portland Cement: ASTM C150/C150M, [Type I] [Type II] [or] [Type III].

          - Fly Ash: ASTM C618, Class C or F.

          - Normal-Weight Aggregate: ASTM C33/C33M, [3/4-inch (19-mm)] [3/8-inch (10-mm)] <Insert dimension> nominal maximum aggregate size.

Delete "Normal-Weight Aggregate" Subparagraph above and retain "Foaming Agent" Subparagraph below if cellular, low-density, controlled low-strength material is required.

          - Foaming Agent: ASTM C869/C869M.

          - Water: ASTM C94/C94M.

Delete "Air-Entraining Admixture" Subparagraph below for cellular, low-density, controlled low-strength material using foaming agent.

          - Air-Entraining Admixture: ASTM C260/C260M.

Retain one of two paragraphs below.

        - Produce cellular, low-density, controlled low-strength material with the following physical properties:

Properties in "As-Cast Unit Weight" and "Compressive Strength" subparagraphs below are based on a range of proportions published by various foam manufacturers. Revise or insert other physical properties for a particular application if required.

          - As-Cast Unit Weight: [30 to 36 lb/cu. ft. (480 to 576 kg/cu. m)] [36 to 42 lb/cu. ft. (576 to 675 kg/cu. m)] <Insert unit weight range> at point of placement, when tested according to ASTM C138/C138M.

          - Compressive Strength: [80 psi (550 kPa)] [140 psi (965 kPa)] <Insert value>, when tested according to ASTM C495/C495M.

Insert other physical properties, in addition to compressive strength in paragraph below, if required for a particular application.

        - Produce conventional-weight, controlled low-strength material with [80-psi (550-kPa)] [140-psi (965-kPa)] <Insert value> compressive strength when tested according to ASTM C495/C495M.

      - GEOFOAM

Retain one or more paragraphs in this article to suit Project.

Compressive strengths in "Extruded-Polystyrene Board Insulation" and "Molded-Polystyrene Board Insulation" paragraphs below are the compressive resistance at 10 percent deformation according to ASTM C578. Verify availability of type of insulation.

        - Extruded-Polystyrene Board Insulation: ASTM C578, [Type IV, 1.55-lb/cu. ft. (25-kg/cu. m) density, 25-psi (173-kPa) compressive strength] [Type X, 1.30-lb/cu. ft. (21-kg/cu. m) density, 15-psi (104-kPa) compressive strength] [Type VI, 1.80-lb/cu. ft. (29-kg/cu. m) density, 40-psi (276-kPa) compressive strength] [Type VII, 2.20-lb/cu. ft. (35-kg/cu. m) density, 60-psi (414-kPa) compressive strength] [Type V, 3.00-lb/cu. ft. (48-kg/cu. m) density, 100-psi (690-kPa) compressive strength].

        - Molded-Polystyrene Board Insulation: ASTM C578, [Type I, 0.90-lb/cu. ft. (15-kg/cu. m) density, 10-psi (69-kPa) compressive strength] [Type VIII, 1.15-lb/cu. ft. (18-kg/cu. m) density, 13-psi (90-kPa) compressive strength] [Type II, 1.35-lb/cu. ft. (22-kg/cu. m) density, 15-psi (104-kPa) compressive strength].

Retain subparagraph below if requiring molded polystyrene to deter termites.

          - Manufacture molded polystyrene with an inorganic mineral registered with the EPA and suitable for application as a termite deterrent.

AFM Corporation, and perhaps other manufacturers, offer products that meet requirements in first paragraph below. ASTM D6817 lists compressive resistances at 1, 5, and 10 percent deformation.

        - Rigid Cellular Polystyrene Geofoam: ASTM D6817, [Type EPS 19, 1.15-lb/cu. ft. (18.4-kg/cu. m) density, 5.8-psi (40-kPa) compressive strength at 1 percent deformation; 16-psi (110-kPa) compressive strength at 10 percent deformation] [Type EPS 39, 2.40-lb/cu. ft. (38.4-kg/cu. m) density, 15-psi (103-kPa) compressive strength at 1 percent deformation; 40-psi (276-kPa) compressive strength at 10 percent deformation] <Insert requirement>.

To limit displacement of insulation or geofoam blocks, connectors may be used. Multibarbed, galvanized-steel sheet connectors in first option in "Connectors" Paragraph below are manufactured by AFM Corporation and perhaps other manufacturers. Steel reinforcing bars in second option may also be used.

        - Connectors: [Geofoam manufacturer's multibarbed, galvanized-steel sheet connectors] [Deformed steel reinforcing bars, 3/4 inch (19 mm) in diameter] <Insert requirement>.

      - ACCESSORIES

Retain one or both of "Warning Tape" and "Detectable Warning Tape" paragraphs in this article to suit Project. Use of warning tapes may be mandatory for underground hazardous utilities.

        - Warning Tape: Acid- and alkali-resistant, polyethylene film warning tape manufactured for marking and identifying underground utilities, 6 inches (150 mm) wide and 4 mils (0.1 mm) thick, continuously inscribed with a description of the utility; colored as follows:

Revise colors below to comply with local practice or requirements of authorities having jurisdiction.

          - Red: Electric.

          - Yellow: Gas, oil, steam, and dangerous materials.

          - Orange: Telephone and other communications.

          - Blue: Water systems.

          - Green: Sewer systems.

        - Detectable Warning Tape: Acid- and alkali-resistant, polyethylene film warning tape manufactured for marking and identifying underground utilities, a minimum of 6 inches (150 mm) wide and 4 mils (0.1 mm) thick, continuously inscribed with a description of the utility, with metallic core encased in a protective jacket for corrosion protection, detectable by metal detector when tape is buried up to 30 inches (750 mm) deep; colored as follows:

Revise colors below to comply with local practice or requirements of authorities having jurisdiction.

          - Red: Electric.

          - Yellow: Gas, oil, steam, and dangerous materials.

          - Orange: Telephone and other communications.

          - Blue: Water systems.

          - Green: Sewer systems.

- EXECUTION

      - PREPARATION

        - Protect structures, utilities, sidewalks, pavements, and other facilities from damage caused by settlement, lateral movement, undermining, washout, and other hazards created by earth-moving operations.

        - Protect and maintain erosion and sedimentation controls during earth-moving operations.

        - Protect subgrades and foundation soils from freezing temperatures and frost. Remove temporary protection before placing subsequent materials.

      - DEWATERING

        - Provide dewatering system of sufficient scope, size, and capacity to control hydrostatic pressures and to lower, control, remove, and dispose of ground water and permit excavation and construction to proceed on dry, stable subgrades.

        - Prevent surface water and ground water from entering excavations, from ponding on prepared subgrades, and from flooding Project site and surrounding area.

        - Protect subgrades from softening, undermining, washout, and damage by rain or water accumulation.

          - Reroute surface water runoff away from excavated areas. Do not allow water to accumulate in excavations. Do not use excavated trenches as temporary drainage ditches.

        - Dispose of water removed by dewatering in a manner that avoids endangering public health, property, and portions of work under construction or completed. Dispose of water and sediment in a manner that avoids inconvenience to others.

      - EXPLOSIVES

        - Explosives:

Retain one of two subparagraphs below. Retain second subparagraph if explosives are permitted.

          - Do not use explosives.

          - Obtain written permission from authorities having jurisdiction before bringing explosives to Project site or using explosives on Project site.

            - Perform blasting without damaging adjacent structures, property, or site improvements.

            - Perform blasting without weakening the bearing capacity of rock subgrade and with the least-practicable disturbance to rock to remain.

      - EXCAVATION, GENERAL

Retain "Unclassified Excavation" or "Classified Excavation" Paragraph below. Retain first paragraph if excavation is unclassified and no changes in the Contract Sum or the Contract Time will be authorized for rock excavation. Retain second paragraph if excavation is classified and adjustments in the Contract Sum and, if applicable, the Contract Time will be authorized for rock excavation. See Evaluations.

        - Unclassified Excavation: Excavate to subgrade elevations regardless of the character of surface and subsurface conditions encountered. Unclassified excavated materials may include rock, soil materials, and obstructions. No changes in the Contract Sum or the Contract Time will be authorized for rock excavation or removal of obstructions.

          - If excavated materials intended for fill and backfill include unsatisfactory soil materials and rock, replace with satisfactory soil materials.

          - Remove rock to lines and grades indicated to permit installation of permanent construction without exceeding the following dimensions:

Measurements in subparagraphs below are examples only; revise to suit Project conditions and office standards.

            - [24 inches (600 mm)] <Insert dimension> outside of concrete forms other than at footings.

            - [12 inches (300 mm)] <Insert dimension> outside of concrete forms at footings.

            - [6 inches (150 mm)] <Insert dimension> outside of minimum required dimensions of concrete cast against grade.

            - Outside dimensions of concrete walls indicated to be cast against rock without forms or exterior waterproofing treatments.

            - [6 inches (150 mm)] <Insert dimension> beneath bottom of concrete slabs-on-grade.

            - [6 inches (150 mm)] <Insert dimension> beneath pipe in trenches and the greater of [24 inches (600 mm)] <Insert dimension> wider than pipe or [42 inches (1065 mm)] <Insert dimension> wide.

        - Classified Excavation: Excavate to subgrade elevations. Material to be excavated will be classified as earth and rock. Do not excavate rock until it has been classified and cross sectioned by Architect. The Contract Sum will be adjusted for rock excavation according to unit prices included in the Contract Documents. Changes in the Contract Time may be authorized for rock excavation.

Revise description in first subparagraph below if removal of surface features and underground utility structures is specified in Section 024116 "Structure Demolition" or Section 311000 "Site Clearing."

          - Earth excavation includes excavating pavements and obstructions visible on surface; underground structures, utilities, and other items indicated to be removed; and soil, boulders, and other materials not classified as rock or unauthorized excavation.

            - Intermittent drilling; blasting, if permitted; ram hammering; or ripping of material not classified as rock excavation is earth excavation.

          - Rock excavation includes removal and disposal of rock. Remove rock to lines and subgrade elevations indicated to permit installation of permanent construction without exceeding the following dimensions:

Measurements in subparagraphs below are examples only; revise to suit Project conditions and office standards and coordinate with rock measurement for unit prices, if any.

            - [24 inches (600 mm)] <Insert dimension> outside of concrete forms other than at footings.

            - [12 inches (300 mm)] <Insert dimension> outside of concrete forms at footings.

            - [6 inches (150 mm)] <Insert dimension> outside of minimum required dimensions of concrete cast against grade.

            - Outside dimensions of concrete walls indicated to be cast against rock without forms or exterior waterproofing treatments.

            - [6 inches (150 mm)] <Insert dimension> beneath bottom of concrete slabs-on-grade.

            - [6 inches (150 mm)] <Insert dimension> beneath pipe in trenches and the greater of [24 inches (600 mm)] <Insert dimension> wider than pipe or [42 inches (1065 mm)] <Insert dimension> wide.

      - EXCAVATION FOR STRUCTURES

Revise tolerances in this article to suit office practice if applicable.

        - Excavate to indicated elevations and dimensions within a tolerance of plus or minus 1 inch (25 mm). If applicable, extend excavations a sufficient distance from structures for placing and removing concrete formwork, for installing services and other construction, and for inspections.

Revise "Excavations for Footings and Foundations" Subparagraph below if footings and foundations are placed on engineered fill.

          - Excavations for Footings and Foundations: Do not disturb bottom of excavation. Excavate by hand to final grade just before placing concrete reinforcement. Trim bottoms to required lines and grades to leave solid base to receive other work.

Retain "Pile Foundations" Subparagraph below if required.

          - Pile Foundations: Stop excavations 6 to 12 inches (150 to 300 mm) above bottom of pile cap before piles are placed. After piles have been driven, remove loose and displaced material. Excavate to final grade, leaving solid base to receive concrete pile caps.

          - Excavation for Underground Tanks, Basins, and Mechanical or Electrical Utility Structures: Excavate to elevations and dimensions indicated within a tolerance of plus or minus 1 inch (25 mm). Do not disturb bottom of excavations intended as bearing surfaces.

Retain "Excavations at Edges of Tree- and Plant-Protection Zones" Paragraph below if required.

        - Excavations at Edges of Tree- and Plant-Protection Zones:

          - Excavate by hand or with an air spade to indicated lines, cross sections, elevations, and subgrades. If excavating by hand, use narrow-tine spading forks to comb soil and expose roots. Do not break, tear, or chop exposed roots. Do not use mechanical equipment that rips, tears, or pulls roots.

          - Cut and protect roots according to requirements in Section 015639 "Temporary Tree and Plant Protection."

      - EXCAVATION FOR WALKS AND PAVEMENTS

        - Excavate surfaces under walks and pavements to indicated lines, cross sections, elevations, and subgrades.

      - EXCAVATION FOR UTILITY TRENCHES

Coordinate this article with utility Sections in other Divisions.

        - Excavate trenches to indicated gradients, lines, depths, and elevations.

          - Beyond building perimeter, excavate trenches to allow installation of top of pipe below frost line.

        - Excavate trenches to uniform widths to provide the following clearance on each side of pipe or conduit. Excavate trench walls vertically from trench bottom to 12 inches (300 mm) higher than top of pipe or conduit unless otherwise indicated.

Revise "Clearance" Subparagraph below to suit Project.

          - Clearance: [12 inches (300 mm) each side of pipe or conduit] [As indicated].

        - Trench Bottoms:

Retain one of first two subparagraphs below. Retain first subparagraph if a bedding course is not required under pipe and conduit; retain second subparagraph if a bedding course is required. Revise to suit Project conditions, requirements of authorities having jurisdiction, type of pipe or conduit, and manufacturer's installation requirements.

          - Excavate and shape trench bottoms to provide uniform bearing and support of pipes and conduit. Shape subgrade to provide continuous support for bells, joints, and barrels of pipes and for joints, fittings, and bodies of conduits. Remove projecting stones and sharp objects along trench subgrade.

            - For pipes and conduit less than 6 inches (150 mm) in nominal diameter, hand-excavate trench bottoms and support pipe and conduit on an undisturbed subgrade.

            - For pipes and conduit 6 inches (150 mm) or larger in nominal diameter, shape bottom of trench to support bottom 90 degrees of pipe or conduit circumference. Fill depressions with tamped sand backfill.

            - For flat-bottomed, multiple-duct conduit units, hand-excavate trench bottoms and support conduit on an undisturbed subgrade.

            - Excavate trenches 6 inches (150 mm) deeper than elevation required in rock or other unyielding bearing material to allow for bedding course.

          - Excavate trenches 4 inches (100 mm) deeper than bottom of pipe and conduit elevations to allow for bedding course. Hand-excavate deeper for bells of pipe.

            - Excavate trenches 6 inches (150 mm) deeper than elevation required in rock or other unyielding bearing material to allow for bedding course.

Retain "Trenches in Tree- and Plant-Protection Zones" Paragraph below if required.

        - Trenches in Tree- and Plant-Protection Zones:

          - Hand-excavate to indicated lines, cross sections, elevations, and subgrades. Use narrow-tine spading forks to comb soil and expose roots. Do not break, tear, or chop exposed roots. Do not use mechanical equipment that rips, tears, or pulls roots.

          - Do not cut main lateral roots or taproots; cut only smaller roots that interfere with installation of utilities.

          - Cut and protect roots according to requirements in Section 015639 "Temporary Tree and Plant Protection."

      - EXCAVATION FOR ELEVATOR CYLINDER

Retain this article if elevator work includes in-ground cylinder but cylinder excavation (normally part of elevator work) is not part of elevator work.

        - Drill well hole plumb in elevator pit to accommodate installation of elevator-cylinder assembly. Coordinate with applicable requirements for diameter and tolerances in [Section 142400 "Hydraulic Elevators."] [Section 142413 "Hydraulic Freight Elevators."]

Well casing in paragraph below is essentially part of Contractor's means and methods unless required by authorities having jurisdiction. Requiring a well casing could help prevent disputes where well-hole excavation is not being provided by elevator Installer.

        - Provide well casing as necessary to retain walls of well hole.

      - SUBGRADE INSPECTION

        - Notify Architect when excavations have reached required subgrade.

        - If Architect determines that unsatisfactory soil is present, continue excavation and replace with compacted backfill or fill material as directed.

Revise locations for proof-rolling in first paragraph below if required; revise type of vehicle and minimum weight to suit Project. Proof-rolling can be used for wide areas, not trenches.

        - Proof-roll subgrade [below the building slabs and pavements] <Insert locations> with a pneumatic-tired [and loaded 10-wheel, tandem-axle dump truck weighing not less than 15 tons (13.6 tonnes)] <Insert requirement> to identify soft pockets and areas of excess yielding. Do not proof-roll wet or saturated subgrades.

          - Completely proof-roll subgrade in one direction[, repeating proof-rolling in direction perpendicular to first direction]. Limit vehicle speed to 3 mph (5 km/h).

          - Excavate soft spots, unsatisfactory soils, and areas of excessive pumping or rutting, as determined by Architect, and replace with compacted backfill or fill as directed.

        - Authorized additional excavation and replacement material will be paid for according to Contract provisions for [unit prices] [changes in the Work].

        - Reconstruct subgrades damaged by freezing temperatures, frost, rain, accumulated water, or construction activities, as directed by Architect, without additional compensation.

      - UNAUTHORIZED EXCAVATION

Revise this article to suit Project.

        - Fill unauthorized excavation under foundations or wall footings by extending bottom elevation of concrete foundation or footing to excavation bottom, without altering top elevation. Lean concrete fill, with 28-day compressive strength of 2500 psi (17.2 MPa), may be used when approved by Architect.

          - Fill unauthorized excavations under other construction, pipe, or conduit as directed by Architect.

      - STORAGE OF SOIL MATERIALS

        - Stockpile borrow soil materials and excavated satisfactory soil materials without intermixing. Place, grade, and shape stockpiles to drain surface water. Cover to prevent windblown dust.

          - Stockpile soil materials away from edge of excavations. Do not store within drip line of remaining trees.

      - BACKFILL

        - Place and compact backfill in excavations promptly, but not before completing the following:

Revise subparagraphs below to suit Project.

          - Construction below finish grade including, where applicable, subdrainage, dampproofing, waterproofing, and perimeter insulation.

          - Surveying locations of underground utilities for Record Documents.

          - Testing and inspecting underground utilities.

          - Removing concrete formwork.

          - Removing trash and debris.

          - Removing temporary shoring, bracing, and sheeting.

          - Installing permanent or temporary horizontal bracing on horizontally supported walls.

        - Place backfill on subgrades free of mud, frost, snow, or ice.

      - UTILITY TRENCH BACKFILL

        - Place backfill on subgrades free of mud, frost, snow, or ice.

        - Place and compact bedding course on trench bottoms and where indicated. Shape bedding course to provide continuous support for bells, joints, and barrels of pipes and for joints, fittings, and bodies of conduits.

Revise dimensions or extent of concrete backfill in "Trenches under Footings" and "Trenches under Roadways" paragraphs below to suit Project.

        - Trenches under Footings: Backfill trenches excavated under footings and within [18 inches (450 mm)] <Insert dimension> of bottom of footings with satisfactory soil; fill with concrete to elevation of bottom of footings. Concrete is specified in Section 033000 "Cast-in-Place Concrete."

        - Trenches under Roadways: Provide [4-inch- (100-mm-)] <Insert dimension> thick, concrete-base slab support for piping or conduit less than [30 inches (750 mm)] <Insert dimension> below surface of roadways. After installing and testing, completely encase piping or conduit in a minimum of [4 inches (100 mm)] <Insert dimension> of concrete before backfilling or placing roadway subbase course. Concrete is specified in Section 033000 "Cast-in-Place Concrete."

        - Backfill voids with satisfactory soil while removing shoring and bracing.

        - Initial Backfill:

Retain "Soil Backfill" or "Controlled Low-Strength Material" Subparagraph below. Retain first subparagraph if specifying soil material as initial backfill; retain second subparagraph if controlled low-strength material is permitted or required as initial backfill.

          - Soil Backfill: Place and compact initial backfill of [subbase material] [satisfactory soil], free of particles larger than [1 inch (25 mm)] <Insert dimension> in any dimension, to a height of 12 inches (300 mm) over the pipe or conduit.

            - Carefully compact initial backfill under pipe haunches and compact evenly up on both sides and along the full length of piping or conduit to avoid damage or displacement of piping or conduit. Coordinate backfilling with utilities testing.

          - Controlled Low-Strength Material: Place initial backfill of controlled low-strength material to a height of 12 inches (300 mm) over the pipe or conduit. Coordinate backfilling with utilities testing.

        - Final Backfill:

Retain "Soil Backfill" Subparagraph below if satisfactory soil material is required as final backfill.

          - Soil Backfill: Place and compact final backfill of satisfactory soil to final subgrade elevation.

Retain "Controlled Low-Strength Material" Subparagraph below if controlled low-strength material is permitted or required as final backfill.

          - Controlled Low-Strength Material: Place final backfill of controlled low-strength material to final subgrade elevation.

Revise tape depths in "Warning Tape" Paragraph below to suit office practice if applicable.

        - Warning Tape: Install warning tape directly above utilities, 12 inches (300 mm) below finished grade, except 6 inches (150 mm) below subgrade under pavements and slabs.

      - SOIL FILL

        - Plow, scarify, bench, or break up sloped surfaces steeper than 1 vertical to 4 horizontal so fill material will bond with existing material.

        - Place and compact fill material in layers to required elevations as follows:

Revise soil materials in subparagraphs below to suit Project. Other soil materials, such as a drainage course or subbase or base courses, may still be required over fill.

          - Under grass and planted areas, use satisfactory soil material.

          - Under walks and pavements, use satisfactory soil material.

          - Under steps and ramps, use engineered fill.

          - Under building slabs, use engineered fill.

Retain subparagraph below if backfill or fill beneath footings and foundations is required. Coordinate material selection with geotechnical engineer's written recommendations.

          - Under footings and foundations, use engineered fill.

        - Place soil fill on subgrades free of mud, frost, snow, or ice.

      - GEOFOAM FILL

Retain this article if geofoam is required.

        - Place a leveling course of sand, [2 inches (50 mm)] <Insert dimension> thick, over subgrade. Finish leveling course to a tolerance of 1/2 inch (13 mm) when tested with a 10-foot (3-m) straightedge.

          - Place leveling course on subgrades free of mud, frost, snow, or ice.

        - Install geofoam blocks in layers with abutting edges and ends and with the long dimension of each block at right angles to blocks in each subsequent layer. Offset joints of blocks in successive layers.

        - Install geofoam connectors at each layer of geofoam to resist horizontal displacement according to geofoam manufacturer's written instructions.

Retain paragraph below if a geotextile cover is required for soil separation or to distribute uplift buoyancy.

        - Cover geofoam with [subdrainage] [separation] geotextile before placing overlying soil materials.

      - SOIL MOISTURE CONTROL

Revise percentages in this article according to geotechnical engineer's written recommendations.

        - Uniformly moisten or aerate subgrade and each subsequent fill or backfill soil layer before compaction to within 2 percent of optimum moisture content.

          - Do not place backfill or fill soil material on surfaces that are muddy, frozen, or contain frost or ice.

In subparagraph below, replace the term "unit weight" with "density" if preferred.

          - Remove and replace, or scarify and air dry, otherwise satisfactory soil material that exceeds optimum moisture content by 2 percent and is too wet to compact to specified dry unit weight.

      - COMPACTION OF SOIL BACKFILLS AND FILLS

Revise depth of layers in first paragraph below to suit Project.

        - Place backfill and fill soil materials in layers not more than [8 inches (200 mm)] <Insert dimension> in loose depth for material compacted by heavy compaction equipment and not more than 4 inches (100 mm) in loose depth for material compacted by hand-operated tampers.

        - Place backfill and fill soil materials evenly on all sides of structures to required elevations and uniformly along the full length of each structure.

Retain one option in paragraph below based on ASTM laboratory-test method required. Replace the term "unit weight" with "density" if preferred.

        - Compact soil materials to not less than the following percentages of maximum dry unit weight according to [ASTM D698] [ASTM D1557]:

Retain applicable subparagraphs below. Percentages of maximum dry unit weight are examples only; revise to suit Project. Delete scarifying and recompacting existing subgrade when proof-rolling will suffice.

          - Under structures, building slabs, steps, and pavements, scarify and recompact top 12 inches (300 mm) of existing subgrade and each layer of backfill or fill soil material at [95] <Insert number> percent.

          - Under walkways, scarify and recompact top 6 inches (150 mm) below subgrade and compact each layer of backfill or fill soil material at [92] <Insert number> percent.

          - Under turf or unpaved areas, scarify and recompact top 6 inches (150 mm) below subgrade and compact each layer of backfill or fill soil material at [85] <Insert number> percent.

          - For utility trenches, compact each layer of initial and final backfill soil material at [85] <Insert number> percent.

      - GRADING

        - General: Uniformly grade areas to a smooth surface, free of irregular surface changes. Comply with compaction requirements and grade to cross sections, lines, and elevations indicated.

          - Provide a smooth transition between adjacent existing grades and new grades.

          - Cut out soft spots, fill low spots, and trim high spots to comply with required surface tolerances.

        - Site Rough Grading: Slope grades to direct water away from buildings and to prevent ponding. Finish subgrades to elevations required to achieve indicated finish elevations, within the following subgrade tolerances:

Revise "Turf or Unpaved Areas," "Walks," and "Pavements" subparagraphs below to suit Project.

          - Turf or Unpaved Areas: Plus or minus [1 inch (25 mm)] <Insert dimension>.

          - Walks: Plus or minus [1 inch (25 mm)] <Insert dimension>.

          - Pavements: Plus or minus [1/2 inch (13 mm)] <Insert dimension>.

        - Grading inside Building Lines: Finish subgrade to a tolerance of [1/2 inch (13 mm)] <Insert dimension> when tested with a 10-foot (3-m) straightedge.

      - SUBSURFACE DRAINAGE

Retain "Subdrainage Pipe," "Subsurface Drain," and "Drainage Backfill" paragraphs below to suit Project; revise to coordinate with Drawings.

Retain "Subsurface Drain" Paragraph below if nonwoven geotextile is used in subsurface drainage applications. Delete if only factory-fabricated drainage panels are used and specified in waterproofing Sections.

        - Subsurface Drain: Place subsurface drainage geotextile around perimeter of subdrainage trench. Place a 6-inch (150-mm) course of filter material on subsurface drainage geotextile to support subdrainage pipe. Encase subdrainage pipe in a minimum of 12 inches (300 mm) of filter material, placed in compacted layers 6 inches (150 mm) thick, and wrap in subsurface drainage geotextile, overlapping sides and ends at least 6 inches (150 mm).

Retain one of two options in subparagraph below if compaction of filter material is required. In first option, revise percentage if required. Replace the term "unit weight" with "density" if preferred.

          - Compact each filter material layer [to 85 percent of maximum dry unit weight according to ASTM D698] [with a minimum of two passes of a plate-type vibratory compactor].

Retain "Drainage Backfill" Paragraph below if using free-draining granular backfill against walls.

        - Drainage Backfill: Place and compact filter material over subsurface drain, in width indicated, to within 12 inches (300 mm) of final subgrade, in compacted layers 6 inches (150 mm) thick. Overlay drainage backfill with one layer of subsurface drainage geotextile, overlapping sides and ends at least 6 inches (150 mm).

Retain one of two options in first subparagraph below if compaction of filter material is required. In first option, revise percentage if required. Replace the term "unit weight" with "density" if preferred.

          - Compact each filter material layer [to 85 percent of maximum dry unit weight according to ASTM D698] [with a minimum of two passes of a plate-type vibratory compactor].

Revise subparagraph below according to geotechnical engineer's written recommendations or delete if no special impervious fill cap is required.

          - Place and compact impervious fill over drainage backfill in 6-inch- (150-mm-) thick compacted layers to final subgrade.

      - SUBBASE AND BASE COURSES UNDER PAVEMENTS AND WALKS

Revise this article to suit Project and for installations of subbase and base courses other than under pavements and walks.

        - Place subbase course[ and base course] on subgrades free of mud, frost, snow, or ice.

        - On prepared subgrade, place subbase course[ and base course] under pavements and walks as follows:

Retain first two subparagraphs below if applicable.

          - Install separation geotextile on prepared subgrade according to manufacturer's written instructions, overlapping sides and ends.

          - Place base course material over subbase course under hot-mix asphalt pavement.

Retain option in four subparagraphs below if retaining "and base course" option in paragraphs above.

          - Shape subbase course[ and base course] to required crown elevations and cross-slope grades.

          - Place subbase course[ and base course] 6 inches (150 mm) or less in compacted thickness in a single layer.

          - Place subbase course[ and base course] that exceeds 6 inches (150 mm) in compacted thickness in layers of equal thickness, with no compacted layer more than 6 inches (150 mm) thick or less than 3 inches (75 mm) thick.

In subparagraph below, replace the term "unit weight" with "density" if preferred.

          - Compact subbase course[ and base course] at optimum moisture content to required grades, lines, cross sections, and thickness to not less than [95] <Insert number> percent of maximum dry unit weight according to [ASTM D698] [ASTM D1557].

Retain "Pavement Shoulders" Paragraph below if required; revise to suit Project. Replace the term "unit weight" with "density" if preferred.

        - Pavement Shoulders: Place shoulders along edges of subbase course[ and base course] to prevent lateral movement. Construct shoulders, at least 12 inches (300 mm) wide, of satisfactory soil materials and compact simultaneously with each subbase[ and base] layer to not less than [95] <Insert number> percent of maximum dry unit weight according to [ASTM D698] [ASTM D1557].

      - DRAINAGE COURSE UNDER CONCRETE SLABS-ON-GRADE

Revise this article to suit Project and for installations of "drainage courses" other than under pavements and walks.

        - Place drainage course on subgrades free of mud, frost, snow, or ice.

        - On prepared subgrade, place and compact drainage course under cast-in-place concrete slabs-on-grade as follows:

Retain applicable subparagraphs below.

          - Install subdrainage geotextile on prepared subgrade according to manufacturer's written instructions, overlapping sides and ends.

          - Place drainage course 6 inches (150 mm) or less in compacted thickness in a single layer.

          - Place drainage course that exceeds 6 inches (150 mm) in compacted thickness in layers of equal thickness, with no compacted layer more than 6 inches (150 mm) thick or less than 3 inches (75 mm) thick.

Revise percentage of compaction in subparagraph below and change compaction test from ASTM D698 to ASTM D4254 or ASTM D1557 if required. Replace the term "unit weight" with "density" if preferred. See the Evaluations.

          - Compact each layer of drainage course to required cross sections and thicknesses to not less than [95] <Insert number> percent of maximum dry unit weight according to ASTM D698.

      - FIELD QUALITY CONTROL

Retain "Special Inspections" Paragraph below if special inspections are required by code and revise to suit requirements of authorities having jurisdiction. Special inspection may not be necessary for fill less than 12 inches (305 mm) deep or outside of foundation or pavement limits; verify with building code and authorities having jurisdiction.

        - Special Inspections: Owner will engage a qualified special inspector to perform the following special inspections:

          - Determine prior to placement of fill that site has been prepared in compliance with requirements.

          - Determine that fill material classification and maximum lift thickness comply with requirements.

          - Determine, during placement and compaction, that in-place density of compacted fill complies with requirements.

          - <Insert special inspections>.

        - Testing Agency: Owner will engage a qualified geotechnical engineering testing agency to perform tests and inspections.

Requirements in remaining paragraphs below, if retained, may actually exceed code-required special inspections. Retain first paragraph below if applicable; revise to suit Project.

        - Allow testing agency to inspect and test subgrades and each fill or backfill layer. Proceed with subsequent earth moving only after test results for previously completed work comply with requirements.

Retain "Footing Subgrade" Paragraph below if applicable; revise to suit Project. If retaining, add other field tests, such as California bearing ratio of subgrades, subbases, and bases for paving, if required.

        - Footing Subgrade: At footing subgrades, at least one test of each soil stratum will be performed to verify design bearing capacities. Subsequent verification and approval of other footing subgrades may be based on a visual comparison of subgrade with tested subgrade when approved by Architect.

Revise first paragraph below to suit Project.

        - Testing agency will test compaction of soils in place according to ASTM D1556, ASTM D2167, ASTM D2937, and ASTM D6938, as applicable. Tests will be performed at the following locations and frequencies:

Frequencies of testing in "Paved and Building Slab Areas," "Foundation Wall Backfill," and "Trench Backfill" subparagraphs below are examples only; revise to suit Project.

          - Paved and Building Slab Areas: At subgrade and at each compacted fill and backfill layer, at least one test for every [2000 sq. ft. (186 sq. m)] <Insert area> or less of paved area or building slab but in no case fewer than three tests.

          - Foundation Wall Backfill: At each compacted backfill layer, at least one test for every [100 feet (30 m)] <Insert dimension> or less of wall length but no fewer than two tests.

          - Trench Backfill: At each compacted initial and final backfill layer, at least one test for every [150 feet (46 m)] <Insert dimension> or less of trench length but no fewer than two tests.

        - When testing agency reports that subgrades, fills, or backfills have not achieved degree of compaction specified, scarify and moisten or aerate, or remove and replace soil materials to depth required; recompact and retest until specified compaction is obtained.

      - PROTECTION

        - Protecting Graded Areas: Protect newly graded areas from traffic, freezing, and erosion. Keep free of trash and debris.

        - Repair and reestablish grades to specified tolerances where completed or partially completed surfaces become eroded, rutted, settled, or where they lose compaction due to subsequent construction operations or weather conditions.

          - Scarify or remove and replace soil material to depth as directed by Architect; reshape and recompact.

        - Where settling occurs before Project correction period elapses, remove finished surfacing, backfill with additional soil material, compact, and reconstruct surfacing.

          - Restore appearance, quality, and condition of finished surfacing to match adjacent work, and eliminate evidence of restoration to greatest extent possible.

      - DISPOSAL OF SURPLUS AND WASTE MATERIALS

Retain one of two paragraphs below.

        - Remove surplus satisfactory soil and waste materials, including unsatisfactory soil, trash, and debris, and legally dispose of them off Owner's property.

        - Transport surplus satisfactory soil to designated storage areas on Owner's property. Stockpile or spread soil as directed by Architect.

          - Remove waste materials, including unsatisfactory soil, trash, and debris, and legally dispose of them off Owner's property.

END OF SECTION 312000